SECTION 21 13 13

WET-PIPE SPRINKLER SYSTEMS

PART 1 - GENERAL

1.01	SUMMARY

A.	Section Includes:

1.	Wet-pipe fire sprinkler system.

2.	Sprinkler piping, fittings, and hangers.

3.	Sprinkler heads.

4.	Alarm valves and accessories.

B.	Related Requirements:

1.	Section 21 05 00 - Common Work Results for Fire Suppression.

2.	Section 21 05 29 - Hangers and Supports for Fire-Suppression Piping and Equipment.

1.02	REFERENCES

A.	NFPA 13-2022 - Standard for the Installation of Sprinkler Systems.

B.	ASTM A53/A53M - Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless.

C.	UL 199 - Automatic Sprinklers for Fire-Protection Service.

1.03	SUBMITTALS

A.	Product Data: Submit manufacturer's technical data for each sprinkler type, valve, and fitting.

B.	Shop Drawings:

1.	Sprinkler system layout showing pipe sizes, sprinkler locations, and hanger locations.

2.	Hydraulic calculations stamped by a licensed fire protection engineer.

3.	Seismic bracing calculations and layout.

C.	Closeout Submittals:

1.	Operation and maintenance manuals.

2.	Contractor's Material and Test Certificate per NFPA 13.

1.04	QUALITY ASSURANCE

A.	Installer Qualifications: Licensed C-16 Fire Protection Contractor in the State of California with minimum 5 years experience on similar K-12 projects.

B.	Design Responsibility: Delegated design by fire protection engineer licensed in California.

C.	Regulatory Requirements: Comply with DSA (Division of the State Architect) requirements.

PART 2 - PRODUCTS

2.01	PIPE AND FITTINGS

A.	Steel Pipe: ASTM A53/A53M, Grade B, Schedule 40, black steel.

B.	Fittings:

1.	Threaded: Cast-iron or malleable-iron, 150 psi rated.

2.	Grooved: Ductile-iron or steel, listed for fire protection service.

2.02	SPRINKLER HEADS

A.	General Requirements:

1.	UL listed and FM approved.

2.	Brass construction with appropriate finish for location.

3.	Temperature rating per NFPA 13 Table 6.2.5.1.

B.	Types:

1.	Concealed pendent: K-factor 5.6, quick-response, white cover plate.

2.	Upright: K-factor 5.6, standard-response, chrome finish.

3.	Sidewall: K-factor 5.6, quick-response, horizontal discharge.

2.03	VALVES

A.	Alarm Check Valve: UL listed, FM approved, complete with trim, retard chamber, and alarm devices.

B.	Control Valves: OS&Y gate valves, UL listed, with tamper switch.

PART 3 - EXECUTION

3.01	EXAMINATION

A.	Verify building structural elements are suitable for hanger attachment.

B.	Confirm ceiling heights and types match design documents.

C.	Do not proceed until unsatisfactory conditions are corrected.

3.02	INSTALLATION

A.	Install in accordance with NFPA 13-2022 and manufacturer's instructions.

B.	Piping:

1.	Slope branch lines toward drain points minimum 1/4 inch per 10 feet.

2.	Provide seismic bracing per NFPA 13 and California Building Code.

3.	Maintain clearances from electrical equipment per NEC.

C.	Sprinkler Heads:

1.	Install perpendicular to ceiling within 1/8-inch tolerance.

2.	Maintain deflector-to-ceiling distances per NFPA 13 Table 8.6.4.1.1.

3.	Coordinate concealed head cover plate color with Architect.

3.03	FIELD QUALITY CONTROL

A.	Hydrostatic Test:

1.	Test at 200 psi for 2 hours.

2.	No leakage or pressure drop permitted.

3.	Repair leaks and retest until satisfactory.

B.	Flush piping before installation of alarm devices and sprinkler heads.

C.	Demonstrate alarm operation to Owner and Fire Marshal.

3.04	CLEANING

A.	Remove construction debris from sprinkler system components.

B.	Clean exposed piping and equipment of dirt, fingerprints, and labels.

3.05	DEMONSTRATION

A.	Train Owner's maintenance personnel on system operation, including:

1.	Alarm valve operation and testing procedures.

2.	Inspector's test connection use.

3.	Sprinkler head replacement procedures.

B.	Provide minimum 2 hours of training.

3.06	SPRINKLER HEAD SCHEDULE

| LOCATION | TYPE | K-FACTOR | TEMP | FINISH |
| --- | --- | --- | --- | --- |
| Classrooms | Concealed Pendent | 5.6 | 155°F | White cover plate |
| Mechanical Rooms | Upright | 5.6 | 200°F | Chrome |
| Corridors | Concealed Pendent | 5.6 | 155°F | White cover plate |
| Kitchen | Pendent | 5.6 | 200°F | Chrome |

END OF SECTION 21 13 13